## PPM Planner (2)
| Alba Facilities Services |  | Registers of Scotland - Meadowbank House, Edinburgh - PPM Planner
v3.6 - (2020)
|  |  | Month | [15 empty] | M | [7 empty] | 6M |  |  |  | 1W
|  | Contractor | Week | W | W |  |  |  | M | M |  |  | Q | Q |  |  |  | A | A
| Category |  | PPM task (ALBA) | January - WC 30/12 |  |  |  |  | February - WC 03/02 |  |  |  | March - WC 02/03 |  |  |  |  | April - WC 6/4 |  |  |  | May - WC 4/5 |  |  |  | June - WC 1/6 |  |  |  |  | July - WC 6/7 |  |  |  | August - WC 3/8 |  |  |  |  | Septemeber - WC 7/9 |  |  |  | October - WC 5/10 |  |  |  | Novemeber - WC 2/11 |  |  |  |  | December WC 7/12 |  |  | Subcontractor | notes
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52
1 | Fire Safety | ALBA - on-site engineer | Emergency Lighting Test - MONTHLY flick tests and record in log book - Lev 7, 6 & 5 (week 1 of month) | bar: January - WC 30/12 2; February - WC 03/02 6; March - WC 02/03 10; April - WC 6/4 15; May - WC 4/5 19; June - WC 1/6 23; July - WC 6/7 28; August - WC 3/8 32; Septemeber - WC 7/9 37; October - WC 5/10 41; Novemeber - WC 2/11 45; December WC 7/12 50
2 | Fire Safety | ALBA - on-site engineer | Emergency Lighting Test - MONTHLY flick tests and record in log book - Lev 4 & 3 (week 2 of month) | bar: January - WC 30/12 3; February - WC 03/02 7; March - WC 02/03 11; April - WC 6/4 16; May - WC 4/5 20; June - WC 1/6 24; July - WC 6/7 29; August - WC 3/8 33; Septemeber - WC 7/9 38; October - WC 5/10 42; Novemeber - WC 2/11 46; December WC 7/12 51
3 | Fire Safety | ALBA - on-site engineer | Emergency Lighting Test - MONTHLY flick tests and record in log book - Lev 2 & 1 (week 3 of month) | bar: January - WC 30/12 4; February - WC 03/02 8; March - WC 02/03 12; April - WC 6/4 17; May - WC 4/5 21; June - WC 1/6 25; July - WC 6/7 30; August - WC 3/8 34; Septemeber - WC 7/9 39; October - WC 5/10 43; Novemeber - WC 2/11 47; December WC 7/12 52
4 | Fire Safety | ALBA - on-site engineer | Emergency Lighting Test - MONTHLY flick tests and record in log book - Lev 0 and plant rooms (week 4 of month) | bar: January - WC 30/12 5; February - WC 03/02 9; March - WC 02/03 13; April - WC 6/4 18; May - WC 4/5 22; June - WC 1/6 26; July - WC 6/7 31; August - WC 3/8 35; Septemeber - WC 7/9 40; October - WC 5/10 44; Novemeber - WC 2/11 48
5 | Fire Safety | ALBA - on-site engineer | Emergency Lighting Test - ANNUAL 3hr test - Building Wide | bar: August - WC 3/8 32
6 | Fire Safety | DMi | Fire Alarm System | [52 empty] | DMI | bar: January - WC 30/12 5; April - WC 6/4 18; August - WC 3/8 32; October - WC 5/10 44
7 | Fire Safety | MacFire | Fire Extinguishers | [52 empty] | Mac Fire | bar: July - WC 6/7 29
8 | Fire Safety | Compco | Dry Risers | [52 empty] | Compco | bar: July - WC 6/7 31; December WC 7/12 50
9 | Fire Safety | Compco / Robon | Fire Suppression (Date Centre 3E-01S) | [52 empty] | Compco | bar: July - WC 6/7 31; December WC 7/12 50
10 | Fire Safety | tbc | Fire Dampers - automatic fire barriers within the ventilation ducting systems | bar: August - WC 3/8 32
11 | Fire Safety | Gmi | Gas Detection (PPM addition) - Boiler House & Gas Meter Room | bar: August - WC 3/8 36
12 | Fire Safety | ALBA - on-site engineer | Fire Doors - Functional Checks - log book input | bar: February - WC 03/02 9; May - WC 4/5 22; August - WC 3/8 36; Novemeber - WC 2/11 49
13 | Security | DMi | Intruder Alarm | [52 empty] | DMI | bar: January - WC 30/12 4; July - WC 6/7 30
14 | Security | DMi | CCTV | [52 empty] | DMI | bar: January - WC 30/12 4; July - WC 6/7 30
15 | Security | DMi | Door Access Control System (Swipe Card - Paxton System) | [52 empty] | DMI | bar: July - WC 6/7 30
16 | Security | Connect AD / mechdoors | Automatic Motorised Doors & Roller Doors | [52 empty] | Connect AD | bar: February - WC 03/02 7; August - WC 3/8 36
17 | Security | Connect AD / mechdoors | Barriers - Speed Gates - Glass Security Gates - Swipe Access - Lev 2 public area - mechanical / operational maintenance | [52 empty] | Connect AD | bar: February - WC 03/02 7; August - WC 3/8 36
18 | Lifts | Thyssen Krupp | Lifts - Elevators - MONTHLY | [52 empty] | Thyssen Krupp | bar: January - WC 30/12 1; February - WC 03/02 6; March - WC 02/03 10; April - WC 6/4 15; May - WC 4/5 19; June - WC 1/6 23; July - WC 6/7 28; August - WC 3/8 32; Septemeber - WC 7/9 37; October - WC 5/10 41; Novemeber - WC 2/11 45; December WC 7/12 50
19 | Lighting internal | ALBA - on-site engineer | Lighting - Internal - general walkround checks | bar: January - WC 30/12 1; February - WC 03/02 6; March - WC 02/03 10; April - WC 6/4 15; May - WC 4/5 19; June - WC 1/6 23; July - WC 6/7 28; August - WC 3/8 32; Septemeber - WC 7/9 37; October - WC 5/10 41; Novemeber - WC 2/11 45; December WC 7/12 50
20 | Lighting external | ALBA - on-site engineer | Lighting - External - general walkround checks - Roof floodlights, underbay lights, perimeter wall lights, illuminated signs | bar: January - WC 30/12 2; February - WC 03/02 7; March - WC 02/03 11; April - WC 6/4 16; May - WC 4/5 20; June - WC 1/6 24; July - WC 6/7 29; August - WC 3/8 33; Septemeber - WC 7/9 38; October - WC 5/10 42; Novemeber - WC 2/11 46; December WC 7/12 51
21 | Electrical - resiliency | ALBA - on-site engineer | Generator Maintenance (for Data Centre resilience) - WEEKLY ' OFF LOAD' 5 min ENGINE TURNOVER
22 | Electrical - resiliency | Dieselec Thistle | Generator Maintenance (for Data Centre resilience) - 6 MONTHLY SERVICE - MAJOR (Feb) - MINOR (Aug) | [52 empty] | Dieselec Thistle | bar: February - WC 03/02 6; August - WC 3/8 32
23 | Electrical - resiliency | Dieselec Thistle | Generator Maintenance (for Data Centre resilience) - 6 MONTHLY SERVICE Diesel Fuel sampling fro cryptosporidium | [52 empty] | Dieselec Thistle | bar: February - WC 03/02 6; August - WC 3/8 32
24 | Electrical - resiliency | RMD | UPS - Core UPS Service | [52 empty] | RMD | bar: February - WC 03/02 6; August - WC 3/8 32
25 | Electrical - In-service Insp & Testing | ALBA - on-site engineer | Microwaves - Radiation Leakage Testing (frequency to be confirmed)
26 | Electrical | ALBA - on-site engineer | Hot water supply - Instantaneous elec water heaters - hydroboils - heatrae sadia - tea prep core areas - 11 of appliances total - full service - clean out | bar: February - WC 03/02 6; August - WC 3/8 32
27 | Electrical | ALBA | Thermal Imaging (Distribution Boards) | bar: Novemeber - WC 2/11 45
28 | Electrical | ALBA | Power Supplies - DB's - all Distribution Boards - condition & cable tremination checks - (dead working) | bar: October - WC 5/10 44
29 | Electrical | ALBA | RCD testing - function testing (push button) - RCD's in DB's and local RCD sockets in office wings etc. | bar: February - WC 03/02 9; May - WC 4/5 22; August - WC 3/8 36; October - WC 5/10 44
30 | Electrical | ALBA | RCD testing - trip time testing - RCD's in DB's and local RCD sockets in office wings etc. | bar: October - WC 5/10 44
31 | Electrical | ALBA | Power Supplies - DB's - Section Boards - All sub main section boards - checks | bar: Novemeber - WC 2/11 45
32 | Electrical | ALBA | Power supplies - Electrical supply intake chambers - Main incoming switch boards - air breakers - busbars - switch fuses - service connections & dust levels | bar: Novemeber - WC 2/11 46
33 | Electrical | NCE | Power Supplies - Power factor correction and harmonic filtration units - servicing/clean etc - Electrical main intake area | bar: Novemeber - WC 2/11 47
34 | Electrical - Lightning | earthtec | Lightning Protection | [52 empty] | Earth Tech | bar: June - WC 1/6 26
35 | Safety Systems | earthtec | Mansafe System - Lev 7 roof guardrails & ladders --- Lev 4 sedum room harness wire sytem | [52 empty] | Earth Tech | bar: July - WC 6/7 30
36 | HVAC | ALBA - AC engineer | Air Conditioning Servicing - All Units | bar: February - WC 03/02 7; August - WC 3/8 33
37 | HVAC | ICG | VRF's Sanyo - Gas Fired Units - for all AC systems - VRF's 1,2,3,4 + 5 | bar: February - WC 03/02 7; August - WC 3/8 33
38 | HVAC | ALBA - AC engineer | Gas supply pipework checks | bar: February - WC 03/02 7; August - WC 3/8 33
39 | HVAC | ALBA - AC engineer | Boilers - Atmospheric Gas Burners - free standing Gas Boilers - 2x in Boiler House | bar: February - WC 03/02 7; August - WC 3/8 33
40 | HVAC | ALBA - AC engineer | Hot Water Supply - Calorifiers Service (LEV 0 Boiler House) | bar: February - WC 03/02 7; August - WC 3/8 33
41 | HVAC | ALBA - AC engineer | Inverters - All inverters for heating pumps and AHU's | bar: February - WC 03/02 7; August - WC 3/8 33
42 | HVAC | ALBA - AC engineer | Air Handling Units FULL ANNUAL SERVICE - Lev 0 - AHU 1, AHU 2. - - Lev 7 - AHU roof tank room | bar: February - WC 03/02 7; August - WC 3/8 33
43 | HVAC | ALBA - AC engineer | Ventilation Ducts - internal cleaning | bar: February - WC 03/02 7; August - WC 3/8 33
44 | HVAC | ALBA - AC engineer | Control Panels & Controllers - Multi input controllers | bar: August - WC 3/8 36
45 | Fabric Checks | ALBA - AC engineer | Doors, windows, blinds, carperts etc | bar: January - WC 30/12 5; February - WC 03/02 9; March - WC 02/03 14; April - WC 6/4 18; May - WC 4/5 22; June - WC 1/6 27; July - WC 6/7 31; August - WC 3/8 36; Septemeber - WC 7/9 40; October - WC 5/10 44; Novemeber - WC 2/11 49 to December WC 7/12 50
46 | Fabric | Style Scotland | Partition doors- locations - 6W-03, 5S-03, 3S-07 | [52 empty] | Style Scotland | bar: June - WC 1/6 26
47 | Heat Emitters | ALBA - on-site engineer | Loading Bay Overhead Heater | bar: February - WC 03/02 9; May - WC 4/5 22; August - WC 3/8 36; Novemeber - WC 2/11 49
48 | Heat Emitters | ALBA - on-site engineer | Permieter Heating - LTHW | bar: February - WC 03/02 9; May - WC 4/5 22; August - WC 3/8 36; Novemeber - WC 2/11 49
49 | Heat Emitters | ALBA - on-site engineer | Hand Driers / Hot Air Driers | bar: August - WC 3/8 36
50 | Water Systems - Hot water supply | ALBA - on-site engineer | Calorifiers service / inspection (Lev 0 Boiler House) | bar: Septemeber - WC 7/9 37
51 | Water Systems - Hot water supply | ALBA - on-site engineer | Instantaneous elec water heaters - hydrobolis | bar: Septemeber - WC 7/9 38
52 | Water Systems - Legionella | ALBA - on-site engineer | Flush little used outlets
53 | Water Systems - Legionella | ALBA - on-site engineer | Tap Temps | bar: January - WC 30/12 1; February - WC 03/02 6; March - WC 02/03 10; April - WC 6/4 15; May - WC 4/5 19; June - WC 1/6 23; July - WC 6/7 28; August - WC 3/8 32; Septemeber - WC 7/9 37; October - WC 5/10 41; Novemeber - WC 2/11 45; December WC 7/12 50
54 | Water Systems - Legionella | ALBA - on-site engineer | Hot Water - calorifiers blow down | bar: March - WC 02/03 10; June - WC 1/6 23; Septemeber - WC 7/9 37; December WC 7/12 50
55 | Water Systems - Legionella | ALBA - on-site engineer | Calorifier flow and return temps | bar: January - WC 30/12 1; February - WC 03/02 6; March - WC 02/03 10; April - WC 6/4 15; May - WC 4/5 19; June - WC 1/6 23; July - WC 6/7 28; August - WC 3/8 32; Septemeber - WC 7/9 37; October - WC 5/10 41; Novemeber - WC 2/11 45; December WC 7/12 50
56 | Water Systems - Legionella | ALBA - on-site engineer | Cold water tank inspections | bar: March - WC 02/03 10; Septemeber - WC 7/9 37
57 | Water Systems - Legionella | ALBA - on-site engineer | TMV's checks / cleaning (All toilets, all tmv's under sinks) | bar: Septemeber - WC 7/9 38
58 | Water Systems - Legionella | ALBA - on-site engineer | Showers and spray tap descale & disenfction (9 of showers, LEV 4,3&0 and 1 of sink spray head (Lev 2 Kitchen) | bar: February - WC 03/02 6; May - WC 4/5 19; August - WC 3/8 32; Novemeber - WC 2/11 45
59 | Water Systems - Legionella | ALBA - on-site engineer | Legionella - Water Sampling | [52 empty] | Westfield Caledonia | bar: August - WC 3/8 35
60 | Water Systems - Legionella | ALBA - on-site engineer | Cold water tank inspections | bar: March - WC 02/03 10
61 | Water Systems - LTHW | Rodol | LTHW - Closed System Analysis (LTHW heating system water sampling) | [52 empty] | Rodol | bar: March - WC 02/03 14; June - WC 1/6 27; Septemeber - WC 7/9 40; December WC 7/12 52
62 | Water Systems - Plumbing | Enviroclean | Drain Cleans - External Grounds | [52 empty] | Enviro Clean | bar: March - WC 02/03 14; Septemeber - WC 7/9 40
63 | Plumbing - pipework general | ALBA - on-site engineer | general plumbing pipeworks and accessories (taps etc) - hot & cold - functinal checks / leak checks etc. | bar: January - WC 30/12 1; April - WC 6/4 15; July - WC 6/7 28; October - WC 5/10 41
64 | Plumbing - rainwater stacks | ALBA - on-site engineer | rainwater stacks - Lev 7 rain drain grills & rainwater pipe stacks (within pipe risers) | bar: April - WC 6/4 15; October - WC 5/10 41
65 | Plumbing - waste water stacks | ALBA - on-site engineer | waste water plumbing | bar: April - WC 6/4 16; October - WC 5/10 42
66 | Pumps- General | ALBA - on-site engineer | All general pumps - inspection/clean and note repairs) | bar: May - WC 4/5 21; Novemeber - WC 2/11 47
67 | Pumps - Water pressure boosting | ALBA - on-site engineer | water pressurisation units - inspection / clean etc. | bar: May - WC 4/5 22; Novemeber - WC 2/11 48
68 | Valves - Radiator TRV's | ALBA - on-site engineer | Radiator TRV's (Lev 6W-01 & Lev 6 Kitchen) | bar: April - WC 6/4 18
69 | Ventialation | ALBA - on-site engineer | Ductwork and supply grilles checks (All site) | bar: January - WC 30/12 1; February - WC 03/02 6; March - WC 02/03 10; April - WC 6/4 15; May - WC 4/5 19; June - WC 1/6 23; July - WC 6/7 28; August - WC 3/8 32; Septemeber - WC 7/9 37; October - WC 5/10 41; Novemeber - WC 2/11 45; December WC 7/12 50
70 | Utility Meter Readings | ALBA - on-site engineer | Elec, Gas and Water Meter Readings (Lev 0 - Plant Rooms) | bar: January - WC 30/12 1; February - WC 03/02 6; March - WC 02/03 10; April - WC 6/4 15; May - WC 4/5 19; June - WC 1/6 23; July - WC 6/7 28; August - WC 3/8 32; Septemeber - WC 7/9 37; October - WC 5/10 41; Novemeber - WC 2/11 45; December WC 7/12 50